Drinking water system Report

| TO: | CAO, Council & Public Works Manager |
| --- | --- |
| FROM: | Brad Faught, DWQMS Representative |
| DATE: | July 14, 2025 |
| SUBJECT: | 2nd Quarterly Report 2025 |

Background

Laurentian Valley Water Works manages just over 14 kilometres of water main and branch lines in the Township. Laurentian Valley Water Works received its Certificate #2893 as a Water Distribution System Class 1 in November of 2000. On May 31, 2011 Drinking Water Works Permit 192-201 and License Number 192-201 was issued by the Ministry of Environment for the Laurentian Valley Distribution System. On February 8, 2021 the License & Permit were renewed. The Drinking Water System Information number for Laurentian Valley Water Works is W260007465. This is the second report for 2025.

Laurentian Valley Township has a water servicing agreement with the City of Pembroke. The water is purchased from the City and distributed in the Stafford Village area, part of Pembroke Street East and part of Pembroke Street West. The City treats and tests the water at the Pembroke Filtration Plant on Riverside Drive and tests the water in their distribution system. The Municipality tests the water in its distribution system.

This report and the Certificates of Analysis are available to the general public at the front counter of the Municipal Office at 460 Witt Road during office hours. Information on the City Water Works can be accessed at www.pembroke.ca

Strategic Directions Alignment:

Core Values

|  | Value for money |  | Professionalism |
| --- | --- | --- | --- |
|  | Act with integrity | X | Transparency |

Strategic Directions

|  | Embrace Rural Identity |  | Invest responsibly in assets & programs |
| --- | --- | --- | --- |
|  | Prioritize Communication |  | Enhance active & social living |

Mission/Vision/Other

Testing

The weekly water samples were sent to Caduceon Laboratories Inc. in Ottawa for analysis. Caduceon is an ODWS Accredited laboratory. The results of the analysis are emailed to the Municipality. The following chart is a summary of those test results.

Analysis for the period of April 1, 2025 – July 2, 2025

| Parameter Tested | MAC, IMAC or Standard | # of Samples | # of Adverse Results | Normal Range | Note # |
| --- | --- | --- | --- | --- | --- |
| E, Coli | Nil | 28 | 0 | Absent |  |
| Total Coliforms | Nil | 28 | 0 | < 1/100ml |  |
| Heterotrophic Plate Count | 500 CFU/ ml | 11 | 0 | <2 CFU/ml – 10 CFU/ml |  |
| Residual Chlorine | .05 mg/ml | 96 | 0 | 0.08 – 1.07 mg/l |  |
| Trihalomethanes | 0.10 mg/liter | 1 | 0 | 0.0952 mg/liter | 4/4 avg |
| Haloacetic Acid | 0.05 | 1 | 0 | 0.0524 | 4/4 avg |

In the second quarter of 2024, the municipality paid Caduceon $1871.34 for laboratory services (HST included).

Complaints

There were no complaints in the second quarter of 2025.

Staffing & Training

Laurentian Valley Waterworks has 3 operators certified for Water Distribution 1 and one Operator-in-Training.

Staff attended a course on Performing Inspection and Maintenance of Fire Hydrants

One staff member attended the Mandatory Course for his license renewal

Maintenance

There were 69 locate requests completed in the second quarter, of which 36                identified water lines to be marked.

-There were two calls to turn residential water off for house repairs.

-Assisted City of Pembroke with flushing two of our hydrants from a water main repair at the corner of Willow Drive and Boundary Road.

-Yearly hydrant flushing and valve exercising completed in the 2nd quarter.

-Two new water meters installed that were malfunctioning

Ministry of Environment, Conservation & Parks

New Compliance Officer has been assigned to Laurentian Valley Township.

Construction

No construction activities to report.

Drinking Water Quality Management System

Summary

In the second quarter of 2025, the water works purchased 76,124 cubic meters of water from the City of Pembroke distributed to homes and businesses (2024 Q2 was 60,636 m3). There were no adverse water quality events in the second quarter.

Respectfully Submitted

Township of Laurentian Valley

“Original Signed”

Brad Faught

Quality Management System Representative

Acronyms

ODWS – Ontario Drinking Water Standards

MAC – Maximum Acceptable Concentration

IMAC – Interim Maximum Acceptable Concentration

MECP- Ministry of Energy, Conservation and Parks