Drinking water system Report

| TO: | CAO, Council & Public Works Manager |
| --- | --- |
| FROM: | Brad Faught, Quality Management System Representative |
| DATE: | January 13, 2025 |
| SUBJECT: | 4th Quarterly Report 2025 |

Background

Laurentian Valley Water Works manages just over 14 kilometres of water main and branch lines in the Township. Laurentian Valley Water Works received its Certificate #2893 as a Water Distribution System Class 1 in November of 2000. On May 31, 2011 Drinking Water Works Permit 192-201 and License Number 192-201 was issued by the Ministry of Environment for the Laurentian Valley Distribution System. On November 26, 2025 the License & Permit were renewed. The Drinking Water System Information number for Laurentian Valley Water Works is W260007465. This is the fourth report for 2025.

Laurentian Valley Township has a water servicing agreement with the City of Pembroke. The water is purchased from the City and distributed in the Stafford Village area, part of Pembroke Street East and part of Pembroke Street West. The City treats and tests the water at the Pembroke Filtration Plant on Riverside Drive and tests the water in their distribution system. The Municipality tests the water in its distribution system.

This report and the Certificates of Analysis are available to the general public at the front counter of the Municipal Office at 460 Witt Road during office hours. Information on the City Water Works can be accessed at www.pembroke.ca.

Strategic Directions Alignment:

Core Values

|  | Value for money |  | Professionalism |
| --- | --- | --- | --- |
|  | Act with integrity | X | Transparency |

Strategic Directions

|  | Embrace Rural Identity |  | Invest responsibly in assets & programs |
| --- | --- | --- | --- |
|  | Prioritize Communication |  | Enhance active & social living |

Mission/Vision/Other

Testing

The weekly water samples were sent to Caduceon Laboratories Inc. in Ottawa for analysis. Caduceon is an ODWS Accredited laboratory. The results of the analysis are emailed to the Municipality. The following chart is a summary of those test results.

Analysis for the period of October 2, 2025 – December 31, 2025

| Parameter Tested | MAC, IMAC or Standard | # of Samples | # of Adverse Results | Normal Range | Note # |
| --- | --- | --- | --- | --- | --- |
| E, Coli | Nil | 28 | 0 | Absent |  |
| Total Coliforms | Nil | 28 | 0 | < 1/100ml |  |
| Heterotrophic Plate Count | 500 CFU/ ml | 4 | 0 | <2 CFU/ml – 4 CFU/ml |  |
| Residual Chlorine | .05 mg/ml | 94 | 0 | 0.05 – 1.12 mg/l |  |
| Trihalomethanes | 0.10 mg/liter | 1 | 0 | 0.109 mg/liter | 4/4 avg |
| Haloacetic Acid | 0.08 | 1 | 0 | 0.053 | 4/4 avg |

In the fourth quarter of 2025, the municipality paid Caduceon $1743.04 for laboratory services (HST included).

Complaints

There were no complaints in the fourth quarter.

Staffing & Training

Two operators attended the Eastern Ontario Water Conference, and one operator attended a course for “New Watermain Commissioning”.  OIT wrote and passed their level 1 Water and Wastewater exam.

Maintenance

-There were 24 locate requests completed in the fourth quarter, of which 11 identified water lines to be marked.

-Hydrants and valves were flushed and operated as per our bi-annual program.

Ministry of Environment, Conservation & Parks

THM reading for the fourth quarter in itself was below the limit but when averaged in with the last three quarters it was above the allowable limits.

Construction

One new water service was turned on for a new build on Roy Street W.

Drinking Water Quality Management System

N/A

Summary

In the fourth quarter of 2025, the water works purchased 66,454 cubic meters of water (2024 was 65,881 cubic meters) from the City of Pembroke distributed to homes and businesses.

Respectfully Submitted

Township of Laurentian Valley

“Original Signed”

Brad Faught

Quality Management System Representative

Acronyms

ODWS – Ontario Drinking Water Standards

MAC – Maximum Acceptable Concentration

IMAC – Interim Maximum Acceptable Concentration

MECP- Ministry of Energy, Conservation and Parks